## Vapor
| Input | Vapor Control Valve
| from vendor sheet | Fluid
|  | Tag No. | -
|  | W | kg/h | 3500
|  | P1 | Kg/cm2 g | 12.5
|  | P2 | Kg/cm2 g | 9.1
|  | M | - | 18.02
|  | K(cp/cv) | - | 1.38
|  | T1 | °C | 184
|  | Xt(From Table5 of Exxon (in sheet 4)) | - | 0.7
|  | X | - | 0.25185
|  | P1 | Kg/cm2 a | 13.5
|  | P2 | Kg/cm2 a | 10.1
|  | Delta p | Kg/cm2 | 3.4
|  | P1 | kPa(a) | 1323.81
|  | P2 | kPa(a) | 990.406
|  | Delta p | kPa | 333.404
|  | T1 | °K | 457
|  | N8 | - | 0.948
|  | K.Xt-2.142 |  | 2.0692
|  | Y |  | 0.87828
|  | Cv |  | 31.8645
|  | Vendor calculated |  | 32
|  | Vendor selected |  | 60
Result | below 15 % difference IGC Cal. To Vendor Cal |  |  | TRUE
| below 60% for Equal and 75% for Linear type difference IGC Cal. To Vendor sel. |  |  | TRUE
| below 10% difference IGC Cal. To Vendor Cal. |  |  | TRUE
| Vendor Cal. To Sel. |  |  | 0.53333
Valve Characteristic
| Stem Travel % | linear | equal
Valve % lift by Curve %
| Vendor Travel % checking |  |  | #DIV/0!
linear
equal

## Liquid
| Input | Liquid Control Valve
| from vendor sheet | Fluid
|  | Tag No. | -
|  | W | kg/h | 35000
|  | P1 | Kg/cm2 g | 45
|  | P2 | Kg/cm2 g | 40
|  | SP.G | - | 0.75
|  | P1 | Kg/cm2 a | 46
|  | P2 | Kg/cm2 a | 41
|  | Delta p | Kg/cm2 | 5
|  | P1 | kPa(a) | 4510.76
|  | P2 | kPa(a) | 4020.46
|  | Delta p | kPa | 490.3
|  | Cv |  | 21.1004
|  | Vendor calculated |  | 22
|  | Vendor selected |  | 40
Result | below 15 % difference IGC Cal. To Vendor Cal |  |  | TRUE
| below 60% for Equal and 75% for Linear type difference IGC Cal. To Vendor sel. |  |  | TRUE
| below 10% difference IGC Cal. To Vendor Cal. |  |  | TRUE
| Vendor Cal. To Sel. |  |  | 0.55
Valve Characteristic
| Stem Travel % | linear | equal
Valve % lift by Curve %
| Vendor Travel % checking |  |  | #DIV/0!
linear
equal

## 2 Phase
2 Phase Control Valve
|  | Liquid phase | Fluid
Input |  |  | Tag No. | -
from vendor sheet |  |  | W | kg/h | 25000
|  |  | P1 | Kg/cm2 g | 40
|  |  | P2 | Kg/cm2 g | 35
|  |  | SP.G | - | 0.85
|  |  | P1 | Kg/cm2 a | 41
|  |  | P2 | Kg/cm2 a | 36
|  |  | Delta p | Kg/cm2 | 5
|  |  | P1 | kPa(a) | 4020.46
|  |  | P2 | kPa(a) | 3530.16
|  |  | Delta p | kPa | 490.3
|  |  | Cv |  | 14.1574
Vendor calculated for Liquid
|  | Vapor phase | W | kg/h
|  |  | P1 | Kg/cm2 g
|  |  | P2 | Kg/cm2 g
|  |  | M | -
|  |  | K(cp/cv) | -
|  |  | T1 | °C
|  |  | Xt(From Table5 of Exxon (in 4) ) | -
|  |  | X | - | 0
|  |  | P1 | Kg/cm2 a | 1
|  |  | P2 | Kg/cm2 a | 1
|  |  | Delta p | Kg/cm2 | 0
|  |  | P1 | kPa(a) | 98.06
|  |  | P2 | kPa(a) | 98.06
|  |  | Delta p | kPa | 0
|  |  | T1 | °K | 273
|  |  | N8 | - | 0.948
|  |  | K.Xt-2.142 |  | 0
|  |  | Y |  | #DIV/0!
|  |  | Cv |  | #DIV/0!
Vendor calculated for Vapor
|  | Total Calculated Cv |  |  | #DIV/0!
Vendor total Calculated Cv
Vendor Selected Cv
| Result | Defference between calculated Cv and vendor(%) |  |  | #DIV/0!
|  | below 15 % difference IGC Cal. To Vendor Cal |  |  | worning
|  | below 60% for Equal and 75% for Linear type difference IGC Cal. To Vendor sel. |  |  | #REF!
|  | below 10% difference IGC Cal. To Vendor Cal. |  |  | worning
|  | Vendor Cal. To Sel. |  |  | #REF!
Valve Characteristic
|  | Stem Travel % | linear | equal
Valve % lift by Curve %
|  | Vendor Travel % checking |  |  | #DIV/0!
linear
equal